## Front Page
Equations for IEC 60335-2-40:2022 Ed. 7
This Excel workbook contains the equations from IEC 60335-2-40:2022 Ed. 7 Annex GG, which primarily covers charge limits. It is provided to facilitate the evaluation of charge limits and facilitate the use of IEC 60335-2-40 Ed. 7 in general.
The workbook needs to be used together with the text of IEC 60335-2-40:2022 Ed. 7 to ensure compliance with the standard. It is provided "as is" with no warranties! The equations in IEC 60335-2-40 always prevails.
This workbook is developed by Vonsild Consulting ApS, and not is endorsed by IEC!
Input cells in this workbook are marked with a green background
Results of equations are marked with a yellow background.
Additional results not formally part of the equation are provided with grey background, where relevant.
Feel free to use, modify, copy and share this workbook. If you find it useful then please send me a kind thought!
Best Regards
Asbjørn Vonsild
Vonsild Consulting
Kløvertoften 45,
7100 Vejle, Denmark
Tel. +45 2372 5559
www.vonsild-consulting.com
vonsild@vonsild-consulting.com

## GG.1.2
GG.1.2 | Determination of the case applicable
For A2 and A3 refrigerants, m1, m2, m3 are defined as follows:
| m1 = 4 ´ LFL | (GG.1) | 0.152 | kg
| m2 = 26 ´ LFL | (GG.2) | 0.988 | kg
| m3 = 130 ´ LFL | (GG.3) | 4.94 | kg
where
LFL is the lower flammability limit in kg/m3 for the refrigerant used. |  |  | 0.038
For A2L refrigerants, m1, m2, m3 are defined as follows:
| m1 = 6 ´ LFL | (GG.4) | 1.842 | kg
| m2 = 52 ´ LFL | (GG.5) | 15.964 | kg
| m3 = 260 ´ LFL | (GG.6) | 79.82 | kg
where
LFL is the lower flammable limit in kg/m3 for the refrigerant used. |  |  | 0.307

## GG.1.3.2
GG.1.3.2 | Determination of unventilated room area for appliances using A2L refrigerant
The minimum opening area for natural ventilation, Anv,min, shall not be less than the following:
|  | (GG.7) | 0.057702 | m2
where
Anv,min | is the minimum opening for natural ventilation in m2;
mc | is the actual refrigerant charge of refrigerant in the system in kg; |  | 4 | kg
mmax | is the allowable maximum refrigerant charge in the system in kg, calculated according to Equation GG.8 or m2, whichever is lower; |  | 2.2 | kg
LFL | is the lower flammability limit in kg/m3; |  | 0.307
A | is the room area in m2; |  | 10
M | is the molar mass of the refrigerant in kg/kmol |  | 52
g | is the gravity acceleration of 9,81 m/s2;
29 | is the average molar mass of air in kg/kmol;
104 | is a constant.

## GG.2.1
GG.2 | Requirements for charge limits in unventilated areas
GG.2.1 | General
The maximum refrigerant charge in a room shall be in accordance with the following:
mmax = 2,5 × (LFL)(5/4) × h0 × (A)1/2, not to exceed mmax = CF × LFL × h0 × A
| [0.384971592441586, not to exceed 0.8892] | (GG.8) | 0.38497 | kg
or the required minimum room area Amin to install an appliance with refrigerant charge mc (kg) shall be in accordance with following:
Amin = (mc / (2,5 × (LFL)(5/4) × h0))2, not less than Amin = mc / (CF × LFL × h0)
| [26.0038372897339, not less than 11.2573099415205] | (GG.9) | 26.0038 | m2
where
mc | is the refrigerant charge in appliance, in kg; |  | 0.385 | kg
A | is the room area, in m2; |  | 26 | m2
2.5 | is a constant;
LFL | is the lower flammability limit, in kg/m3; |  | 0.038 | kg/m3
CF | is a concentration factor with a value of 0,75 for refrigerating systems using A2L refrigerant and a value of 0,5 for refrigerating systems using A2 or A3 refrigerant; |  | 0.5
h0 | is the release height, the vertical distance in metres from the floor to the point of release when the appliance is installed (see Figure GG.3). |  | 1.8 | m
h0 = (hinst+hrel) or 0,6 m, whichever is higher.
hrel | is the release offset in metres from the bottom of the appliance to the point of release (see Figure GG.3). Cumulative openings smaller than 5 cm2 and openings with a single dimension of not more than 0,1 mm are not considered as openings where leaking refrigerant can escape. Openings for routing of wires and tubing which are not sealed openings shall include the total area of the opening without consideration of the area occupied by the tubing or wire. |  | 0.1 | m
hinst | is the installed height in metres of the unit (see Figure GG.3). |  | 1.7 | m
Reference installed heights are given below:
hinst = 0,0 m for portable and floor mounted;
hinst = 1,0 m for window mounted;
hinst = 1,8 m for wall mounted;
hinst = 2,2 m for ceiling mounted.

## GG.2.2
GG.2.2 | Appliances using A2L refrigerants with incorporated circulation airflow
The maximum refrigerant charge in a room shall be in accordance with the following:
| mmax = CF × LFL × hra × A | (GG.10) | 3.684 | kg
or the required minimum room area Amin of installed appliance with refrigerant charge mc (kg) shall be in accordance with following;
| Amin = mc/(CF × LFL × hra) | (GG.11) | 6.5147 | m2
where
CF | is a concentration factor with a value of 0,75; |  | 0.75
mc | is the actual refrigerant charge in the system in kg; |  | 3 | kg
hra | is the estimate reaching height of airflow in m; |  | 2 | m
A | is the room area in m2; |  | 8 | m2
LFL | is the lower flammability limit in kg/m3. |  | 0.307 | kg/m3
Table GG.2 – Circulation airflow
| Minimum airflow rate: |  | 293.1596 | m3/h
| ha + hd: |  | 1.3339 | m
| ha is the air delivery height in upper side in m. |  | 0.2
hd is the dynamic reaching height of airflow in m:
|  | (GG.12) | 1.1339 | m
where
v | is the circulation airflow velocity in m/s; |  | 3 | m/s
| is the circulation airflow elevation angle from horizontal in degrees (0° ≤ ≤ 90°); |  | 45 | °
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
| is the gas density of the refrigerant at atmospheric pressure and 25 °C in kg/m3. |  | 2.13 | kg/m3

## GG.2.3
GG.2.3 | Appliances using A2/A3 refrigerants with incorporated circulation airflow
The maximum refrigerant charge in a room shall be in accordance with the following:
| mmax = CF × LFL × A × 2,2 | (GG.13) | 0.45144 | kg
or the required minimum room area Amin of installed appliance with refrigerant charge mc (kg) shall be in accordance with following;
| Amin = mc/(CF × LFL × 2,2) | (GG.14) | 10.7656 | m2
where
CF | is a concentration factor not exceeding 0,5. The value shall be the value as used in the equation for calculating Qmin in Equation GG.15; |  | 0.5
mc | is the actual refrigerant charge in the system in kg; |  | 0.45 | kg
2.2 | is the room height in m;
A | is the room area in m2; |  | 10.8 | m2
LFL | is the lower flammability limit in kg/m3. |  | 0.038 | kg/m3
[CF factor required to get A = Amin: 0.498405103668262]
The fan incorporated into an appliance shall have a minimum circulation airflow according to:
|  | (GG.15) | 406.2661 | m3/h
|  | This is: | 2.5331 | m/s
where
3600 | is a constant
8 | is a constant
A0 | is the discharge area of the airflow in m2. The value is the nominal face area of the outlet. The grille area shall not be deducted; |  | 0.04455 | m2
240 | is a constant based on leaking the total charge in 4 minutes;
mc | is the actual refrigerant charge amount in the system in kg; |  | 0.45 | kg
LFL | is the lower flammability limit in kg/m3; |  | 0.038 | kg/m3
Y | is a constant, if there are leak sources outside the unit Y = 1,5, otherwise Y = 1; |  | 1.5
CF | is a concentration factor specified by the manufacturer and not exceeding 0,5. The value shall be the value as used in Equation (GG.13) and Equation (GG.14) for calculating mmax and Amin. |  | 0.49841

## GG.4
GG.4 | Requirements for mechanical ventilation within the appliance enclosure
The negative pressure measurement in the interior of the appliance enclosure shall be 20 Pa or more and the flow rate to the exterior shall be at least Qmin:
| Qmin = 3 600 × 1 / CF × 24,5/M × ṁleak (with a minimum of 2 m3/h) |  | 33.0082 | m3/h
(GG.16)
where
3 600 | is a conversion of seconds to hours;
CF | is a concentration factor with a value of 0,25;
M | is the molar mass of refrigerant in kg/kmol; |  | 44 | kg/kmol
Qmin | is the minimum required volume flow of the ventilation in m3/h;
24.5 | is the universal gas constant R multiplied by temperature of 298 K (25 °C) and divided by pressure of 101,325 kPa in l/mol;
ṁleak | is the leak rate in kg/s. |  | 0.0041167
For refrigerating systems which are not enhanced tightness refrigerating systems, the leak rate, ṁleak, shall be determined as:
| ṁleak = mc / 240 | (GG.17) | 0.0041167 | kg/s
where
mc | is the refrigerant charge in kg; |  | 0.988 | kg
240 | is the 4 min release time in s.
For enhanced tightness refrigerating systems, the leak rate, ṁleak, shall be determined as:
– for A2L refrigerants ṁleak = 0,00278 kg/s,
– for A2 and A3 refrigerants, the values of GG.14.3.1, Table GG.6 in kg/s.

## GG.7
GG.7 | Factory sealed single package units which are not fixed appliances with a refrigerant charge of m1 < mc £ 2 ´ m1
GG.7.1 | Determination of refrigerant charge
The maximum refrigerant charge in a room shall be in accordance with the following:
| mmax = CF × LFL × A × 2,2 | (GG.18) | 0.3553 | kg
or the required minimum room area, Amin, to install an appliance with refrigerant charge mc shall be in accordance with the following:
| Amin = mc/(CF × LFL × 2,2) | (GG.19) | 14.3541 | m2
where
CF | is a concentration factor with a value of 0,25;
mc | is the refrigerant charge in the appliance in kg; |  | 0.3 | kg
A | is the room area in m2; |  | 17 | m2
LFL | is the lower flammability limit in kg/m3; |  | 0.038 | kg/m3
2.2 | is the minimum ceiling height employed in metres (m).

## GG.8.2
GG.8 | Ventilated area requirements for appliances using A2L refrigerants
GG.8.2 | Natural ventilation to outdoors
The maximum refrigerant charge of a system, mmax, and minimum opening area, Anv,min, for natural ventilation to outdoors shall be calculated using the following equations:
|  | (GG.20) | 97.8954 | kg
|  | (GG.21) | 0.35733 | m2
where
mc | is the refrigerant charge of a system in kg; |  | 50 | kg
Anv | is the opening area in m2; |  | 0.5 | m2
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
0.14 | is a constant derived from the gravity acceleration, flow coefficient, etc.;
0.04 | is the conversion constant from hydrocarbon to other LFL.

## GG.8.3
GG.8 | Ventilated area requirements for appliances using A2L refrigerants
GG.8.3 | Mechanical ventilation requirements for rooms with appliances using A2L refrigerants
The airflow shall be calculated using of the formula below. Losses caused by ducts or other components in the air stream have to be considered.
|  | (GG.22) | 1270.3583 | m3/h
where
Qmin | is the required airflow volume in m3/h;
mmax | is the maximum refrigerant charge for the system in the room in kg according to Equation (GG.8) or m2, whichever is lower, or Clause GG.9 where applicable; |  | 12 | kg
| NOTE m2 is |  | 15.964 | kg
mc | is the actual refrigerant charge of a single refrigerating system expressed in kg; |  | 25 | kg
4 | is the assumed leak time (4 min);
2 | is a safety factor of 2;
60 | is the conversion minutes to hours;
LFL | is the lower flammability limit in kg/m3. |  | 0.307 | kg/m3
Mechanical ventilation shall be made to the outdoor or an indoor space where the room area is larger than the minimum area of the room which the mechanical ventilation exhausts into, EAmin, calculated using the following equation:
| EAmin = (mc - mmax)/(CF × LFL × H) | (GG.23) | 76.9914 | m3
where
CF | is the concentration factor with a value of 0,25;
mc | is the refrigerant charge in kg; |  | 25 | kg
mmax | is the allowable maximum refrigerant charge for the system in the room in kg; |  | 12 | kg
H | is the height of the room = 2,2 m;
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3

## GG.9
GG.9 | Charge limits for appliances using A2L refrigerants connected via an air duct system to one or more rooms
GG.9.1 | General
The minimum airflow shall be determined as:
| Qmin = 60 × mc / LFL | (GG.24) | 3908.7948 | m3/h
where
Qmin | is the minimum circulation airflow circulated to the total conditioned space in m3/h;
mc | is the actual refrigerant charge for a single refrigerating system expressed in kg; |  | 20 | kg
LFL | is the lower flammability limit in kg/m2. |  | 0.307 | kg/m3
The maximum refrigerant charge based on the room area for the total conditioned space shall be in accordance with the following:
| mmax = CF × LFL × H × TA | (GG.25) | 16.885 | kg
or the required minimum total conditioned room area TAmin of installed appliance with refrigerant charge mc (kg) shall be in accordance with following:
| TAmin = mc/(CF × LFL × H) | (GG.26) | 59.2242 | m2
where
CF | is the concentration factor with a value of 0,50;
mmax | is the allowable maximum refrigerant charge in the system in kg;
mc | is the refrigerant charge in appliance in kg; |  | 20 | kg
TAmin | is the required minimum area of the total conditioned space in m2;
H | is the height of the room = 2,2 m;
TA | is the area of the total conditioned space in m2; |  | 50 | m2
LFL | is the lower flammability limit in kg/m3. |  | 0.307 | kg/m3
If TA is smaller than TAmin, additional ventilation according to GG.8.3 shall be employed.

## GG.10
GG.10 | Allowable charge for enhanced tightness refrigerating systems using A2L refrigerant
GG.10.3.1 | Maximum refrigerant charge limit A
The maximum refrigerant charge mmax in a room and the minimum room area Amin of the installed appliance with refrigerant charge mc shall be in accordance with the following:
| mmax = CF × LFL × Hr × A | (GG.27) | 6.14 | kg
| Amin = mc/(CF × LFL × Hr) | (GG.28) | 26.0586 | m2
where
CF | is the concentration factor with a value of 0,50;
mmax | is the maximum refrigerant charge in kg;
mc | is the total refrigerant charge in the refrigerating system in kg; |  | 8 | kg
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
Hr | is the effective height of the indoor unit; |  | 2 | m
A | is the room floor area in m2; |  | 20 | m2
Amin | is the required minimum room area in m2.
The effective height, Hr, of the unit is determined as follows:
· Where the release height, h0, as determined in Clause GG.2 is equal to or greater than 1,8 m or the appliance is with incorporated circulation airflow, the effective height, Hr, is the room height in m but not more than 2,2 m unless h0 is higher than 2,2 m;
· In all other cases the effective height, Hr, is the release height, h0, as determined in Clause GG.2.
For room areas exceeding 250 m2, mmax shall be calculated with a room area (A) of 250 m2.
GG.10.3.2 | Maximum refrigerant charge limit B
The maximum refrigerant charge mmax in a room and the minimum room area Amin of the installed appliance with refrigerant charge mc shall be in accordance with the following:
| mmax = CF × LFL × Hr × A | (GG.29) | 9.21 | kg
| Amin = mc/(CF × LFL × Hr) | (GG.30) | 17.3724 | m2
where
CF | is the concentration factor with a value of 0,75;
mmax | is the maximum refrigerant charge in kg;
mc | is the total refrigerant charge in the refrigerating system in kg; |  | 8 | kg
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
Hr | is the effective height of the indoor unit; |  | 2 | m
A | is the room floor area in m2; |  | 20 | m2
Amin | is the required minimum room area in m2.
The effective height, Hr, of the unit is determined as follows:
· Where the release height, h0, as determined in Clause GG.2 is equal to or greater than 1,8 m or the appliance is with incorporated circulation airflow, the effective height, Hr, is the room height in m but not more than 2,2 m unless h0 is higher than 2,2 m;
· In all other cases the effective height, Hr, is the release height, h0, as determined in Clause GG.2.
For room areas exceeding 250 m2, mmax shall be calculated with a room area (A) of 250 m2.
GG.10.4 | Requirement for units with incorporated circulation airflow to prevent stagnation
GG.10.4.1 | General
The circulation shall operate continuously or be turned on by leak detection systems. The minimum air velocity and minimum airflow shall be as follows:
· Minimum airflow = 240 m3/h;
· There is no minimum circulation airflow velocity requirement for downwards airflow;
· Minimum air velocity for upwards airflow:
| vmin = (– 4,0 × 10-5 × M2 + 0,010 8 × M + 1,42) / sin φ | (GG.31) | 3.7469 | m/s
where
vmin | is the minimum air velocity in m/s;
M | is the molar mass in kg/kmol; |  | 52 | kg/kmol
φ | is the airflow angle above horizontal in degrees, an angle below 15 degrees is considered to be 15 degrees. |  | 30 | °
General requirements for number of measures
GG.10.3.1: Charge is not according to limit A (≤ 50%)
GG.10.3.2: Charge is according to limit B (≤ 75%)
m3

## GG.11
GG.11 | Ventilation for enhanced tightness refrigerating systems using A2L refrigerants
GG.11.1 | General
Where ventilation is to an indoor space, the total area of that space and the space in which the appliance is installed, shall have a total room area not less than Amin according to:
| Amin = mc /(CF × LFL × Hr) | (GG.32) | 26.0586 | m2
where
CF | is the concentration factor with a value of 0,50;
mc | is the total refrigerant charge in the refrigerating system in kg; |  | 8 | kg
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
Hr | is the effective height of the indoor unit in m; |  | 2 | m
Amin | is the required minimum room area in m2.
The effective height, Hr, of the unit is determined as follows:
· Where the release height, h0, as determined in Clause GG.2 is equal to or greater than 1,8 m or the appliance is with incorporated circulation airflow, the effective height, Hr, is the room height in m but not more than 2,2 m unless h0 is higher than 2,2 m;
· In all other cases the effective height, Hr, is the release height, h0, as determined in Clause GG.2.
GG.11.2 | Natural ventilation
The minimum opening area for natural ventilation (Anv,min) to an indoor space shall be:
|  | (GG.33) | 0.012277 | m2
|  | this is | 122.7715 | cm2
where
Anv,min | is the minimum required natural ventilation opening area in m2;
M | molar mass in kg/kmol; |  | 52 | kg/kmol
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
720 | is the coefficient resulting from calculating all the constants used to establish the formula;
29 | is the average molar mass of air in kg/kmol.
The minimum opening area for natural ventilation (Anv,min) to an outdoor space shall be:
|  | (GG.34) | 0.14293 | m2
|  | this is | 1429.3344 | cm2
where
mc | is the refrigerant charge of a system in kg; |  | 8 | kg
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
0.14 | is a constant derived from the gravity acceleration, flow coefficient, etc.;
0.04 | is the conversion constant from hydrocarbon to other LFL.
GG.11.3 | Mechanical ventilation
GG.11.3.2 | Required airflow
For (Qmin × 0,25 × LFL)/10 < 1, the airflow of the mechanical ventilation shall be at least the quantity that satisfies the following formula:
|  | (GG.35) | TRUE
| mc allowed is |  | 10.001 | kg
| Qmin allowed is approx. |  | 124.4959 | m3/h
For (Qmin × 0,25 × LFL)/10 ≥ 1, the airflow shall be determined according the following formula:
|  | (GG.36) | 130.2932 | m3/h
where
mc | is the refrigerant charge, expressed in kg; |  | 10 | kg
V | is the room volume in m3; |  | 40 | m3
10 | is the expected maximum leak rate in kg/h;
Qmin | is the ventilation airflow in m3/h; |  | 124.498 | m3/h
LFL | is the lower flammability limit in kg/m3. |  | 0.307 | kg/m3
| a |  | 3.2573
| z in W0(z) |  | 0.12538
| W0(z) approx. |  | 0.11212
| Q_min allowed approx: |  | 125.8085
| D m_c |  | 0.7119
| D m_c/D Q_min |  | 0.62381
| Q_min allowed 2nd approx: |  | 124.6673
| D m_c |  | 0.082541
| D m_c/D Q_min |  | 0.48944
| Q_min allowed 3rd approx: |  | 124.4986
| D m_c |  | 0.0013035
| D m_c/D Q_min |  | 0.47414
| Q_min allowed 4th approx: |  | 124.4959
| D m_c (error) |  | 3.3271e-07

## GG.12
GG.12 | Safety shut-off valves for enhanced tightness refrigerating systems using A2L refrigerants
For appliances which are not on the lowest underground floor, where the release height, h0, as determined in Clause GG.2 is equal to or greater than 1,8 m or the appliance is with integral circulation airflow, the releasable charge as determined by Annex QQ shall be limited to:
| mrl < CF × LFL × Hr × A | (GG.37) | 9.21 | kg
where
CF | is the concentration factor with a value of 0,75;
mrl | is the releasable charge in kg;
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
Hr | is the effective height of the indoor unit as determined in GG.10.3; |  | 2 | m
A | is the room floor area in m2. |  | 20 | m2
For all other appliances, the releasable charge as determined by Annex QQ shall be limited to:
| mrl < CF × LFL × Hr × A | (GG.38) | 6.14 | kg
where
CF | is the concentration factor with a value of 0,50;
mrl | is the releasable charge in kg;
LFL | is the lower flammability limit in kg/m3; |  | 0.307 | kg/m3
Hr | is the effective height of the indoor unit as determined in GG.10.3; |  | 2 | m
A | is the room floor area in m2. |  | 20 | m2

## GG.14.2
GG.14 | Allowable charge for enhanced tightness refrigerating systems using A2 or A3 refrigerant
GG.14.2 | Requirement for enhanced tightness units without incorporated circulation airflow
For enhanced tightness refrigeration systems the maximum refrigerant charge in a room shall be in accordance with the following:
| mmax = CF × LFL × A × h0 | (GG.39) | 0.9576 | kg
or the required minimum room area Amin of installed appliance with refrigerant charge mc shall be in accordance with following;
| Amin = mc/(CF × LFL × h0) | (GG.40) | 20.8855 | m2
where
CF | is a concentration factor with a value of 0,35;
mc | is the actual refrigerant charge in the system in kg; |  | 0.5 | kg
h0 | is the release height, the vertical distance in metres from the floor to the point of release when the appliance is installed (see Figure GG.3) according to Clause GG.2.1 but not less than 0,6 m and not to exceed 2,2 m; |  | 1.8 | m
A | is the room area in m2; |  | 40
LFL | is the lower flammability limit in kg/m3. |  | 0.038 | kg/m3

## GG.14.3
GG.14 | Allowable charge for enhanced tightness refrigerating systems using A2 or A3 refrigerant
GG.14.3 | Requirement for enhanced tightness units with incorporated circulation airflow
For enhanced tightness refrigeration systems, the maximum refrigerant charge in a room shall be in accordance with the following:
| mmax = CF × LFL × A × 2,2 | (GG.41) | 0.45144 | kg
or the required minimum room area Amin of installed appliance with refrigerant charge mc shall be in accordance with following;
| Amin = mc /(CF × LFL × 2,2) | (GG.42) | 10.7656 | m2
where
CF | is a concentration factor not exceeding 0,5. The value shall be the value as used in the equation for calculating Qmin in Equation GG.43; |  | 0.5
mc | is the actual refrigerant charge in the system in kg; |  | 0.45 | kg
2.2 | is the room height in m;
A | is the room area in m2; |  | 10.8
LFL | is the lower flammability limit in kg/m3. |  | 0.038 | kg/m3
The minimum circulation airflow shall be determined as:
|  | (GG.43) | 354.976 | m3/h
|  | This is: | 1.0956 | m/s
where
3600 | is a constant
A0 | is the discharge area of the airflow in m2. The value is the nominal face area of the outlet. The grille area shall not be deducted; |  | 0.09 | m2
Y | is a constant, if there are leak sources outside the unit Y = 1,5, otherwise Y = 1; |  | 1
ṁleak | is the refrigerant leak rate as determined in Table GG.6 in kg/s; |  | 0.00112 | kg/s
h0 | is the release height, the vertical distance in metres from the floor to the point of release when the appliance is installed (see Figure GG.3) according to Clause GG.2.1 but not less than 0,6 m and not to exceed 2,2 m; |  | 1.5 | m
LFL | is the lower flammability limit in kg/m3; |  | 0.038
CF | is a concentration factor not exceeding 0,5. The value shall be the value as used in Equation GG.41 and Equation GG.42 for calculating Amin and mmax. |  | 0.49841
For refrigerants not listed in Table GG.6, leak mass flow rate (ṁleak) is calculated from:
| x 10-6 | (GG.44) | 0.0026627 | kg/s
| Note that there is an error in Equation GG.44! | This is: | 159.7598 | g/min
where |  |  | 9.5856 | kg/h
167 | is a reference leak mass flow rate in g/min;
432 | is a coefficient;
Ṁs | is the choked flow mass flux in kg/m2s. |  | 6887.8463 | kg/m2s
The choked flow mass flux, Ṁs, is:
|  | (GG.45) | 6887.8463 | kg/m2s
where
0.61 | is the discharge coefficient;
k | is the ratio of specific heats of refrigerant vapour; |  | 2.03
ρ0 | is the density of saturated refrigerant vapour at 45 °C in kg/m3 at the system pressure p0; |  | 80 | kg/m3
p0 | is the pressure in the system at 45 °C in Pa. |  | 2664708 | Pa